## Calculation
SIF Determination
Please Note that this determination is only for 1 SIF.
DGC06 & SC2-34XX (Flammable Gases) |  |  | Output
|  | Units |  |  | Units
HFT | 0 |  | HFT | 0
PFD |  | --select-- | PFD |  | --select--
SFF | 95% | % Percent | SFF | 95% | % Percent
λ DU | 1.38e-07 | --select-- | λ DU | 1.38e-07 | --select--
λ SU |  | --select-- | λ SU |  | --select--
λ SD |  | --select-- | λ SD |  | --select--
PFT | 1 | Year | PFT | 1 | Year
MTTR |  | Hours | MTTR |  | Hours
* Only the fields highlighted Red are required. |  |  | * Only the fields highlighted Red are required.
| Required SIL: | 1
Note on A11: Hardware Fault Tolerance: Default = 0, However can be 1 if two sensors are used in the same location (reduncancy)
Note on E11: Hardware Fault Tolerance: Default = 0, However can be 1 if two sensors are used in the same location (reduncancy)
Note on A12: Random Failure Rate: Probability of Failure on demand Average - Probability that a system will fail dangerously and not be able to perform its safety function when required.
Note on E12: Random Failure Rate: Probability of Failure on demand Average - Probability that a system will fail dangerously and not be able to perform its safety function when required.
Note on A13: Safety Failure Fraction: The fraction of the overall failure rate of a device that results in either a safe fault or a diagnosed (detected) unsafe fault.
Note on E13: Safety Failure Fraction: The fraction of the overall failure rate of a device that results in either a safe fault or a diagnosed (detected) unsafe fault.
Note on A14: Failure Rate λ DU: Dangerous Undetected Failures
Note on E14: Failure Rate λ DU: Dangerous Undetected Failures
Note on A15: Failure Rate λ SU: Safe Undetected Failures
Note on E15: Failure Rate λ SU: Safe Undetected Failures
Note on A16: Failure Rate λ SD: Safe Detected Failures
Note on E16: Failure Rate λ SD: Safe Detected Failures
Note on A17: Proof Test Interval: Time between verifying the components work and restoring component to as new.
Note on E17: Proof Test Interval: Time between verifying the components work and restoring component to as new.
Note on A18: Mean Time To Recover: Time taken to restabilise system after a dangerous failure.
Note on E18: Mean Time To Recover: Time taken to restabilise system after a dangerous failure.
Note on B22: Required SIL: SIL determined as per HAZOP determination

## Units
Units | Sensor + Controller + Relay
Per Hour | DGC06 & SC2-34XX (Flammable Gases)
Per Annum | DGC06 & SC2-11XX (Toxic Gases)
Per Billion Hrs
Output Device
Solenoid
Alarm
Ventilation Fans
Other